


	Scottish Water GcS Checklist 

	Check
	Provided (Y/N)

	Summary details

	Acceptable (Y/N)
Internal Use Only
	Comments / remedial actions
Internal Use Only

	Dimensions

	Length (m)
	
	
	
	

	Width (m)
	
	
	
	

	Depth to base – maximum (3m)
	
	
	
	

	Longitudinal base slope (1 in ?)
	
	
	
	

	Cover level – is the cover level over the GCS between a minimum of 500 mm and a maximum of 1000 mm?
	
	
	
	

	Geometry of GCS – is the shape cuboid?
	
	
	
	

	Distance – from the nearest structure and land boundary, is there a minimum of five metres of clear open public space around the GCS both above and below?
	
	
	
	

	Inflows

	Provide a description of the contributing catchment land used and its size (m²) (industrial/commercial to be noted)
	
	
	
	

	Sedimentation control – design details of the silt trap provided?
	
	
	
	

	Any other upstream SUDS treatment to reduce sedimentation (Y/N); if yes, details provided?
	
	
	
	

	Any Planting – as per SfS Appendix XIII
	
	
	
	

	Outfall Arrangements 

	Flow control MH flow rate (l/s)
	
	
	
	

	Flood route plan provided 
	
	
	
	

	Storage

	Storage sizing – evidence that system has been sized to 1:30 year return period plus 15% loss of storage?
	
	
	
	

	Structural

	Confirm type of unit or structure to be used (manufacturer + product type) + BBA certification
	
	
	
	

	Design life – data sheet or written confirmation from manufacturer provided? (60 year minimum)
	
	
	
	

	Groundwater level (m) and flotation – groundwater table levels supplied; confirm if GCS is affected by groundwater. If yes, flotation calculations and mitigations must be provided and confirmed.
	
	
	
	

	Confirm that calculations are provided to demonstrate acceptable structural capacity over the proposed system design life that are approved by an engineer
	
	
	
	

	Has sufficient venting been provided to allow excess air pressure to be released when the GCS units fill?
	
	
	
	

	Critical materials and product specifications 

	Geomembrane
	
	
	
	

	Topsoil spec confirmed 
	
	
	
	

	Vehicle Access

	Accommodate a 32 tonne tanker (load rating)
	
	
	
	

	Reversing only for parking purposes (to be considered on a site-by-site basis)
	
	
	
	

	Access adjacent to the GCS and not over any part of the structure
	
	
	
	

	Full swept path analysis provided
	
	
	
	

	Parking within 20 metres of silt trap and flow control manhole
	
	
	
	

	Surface finish confirmed (provide detail)
	
	
	
	

	Maintainability 

	Confirm that access for maintenance is acceptable
	
	
	
	

	Can the GCS be jetted? (product data sheet from manufacturer to confirm)
	
	
	
	

	Can the GCS be CCTV inspected? (product data sheet from manufacturer to confirm)
	
	
	
	

	Are there any specific features that are likely to pose maintenance difficulties? If yes, identify mitigation measures required
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