| Scottish Water GcS Checklist |  |  |  |  |
| --- | --- | --- | --- | --- |
| Check | Provided (Y/N) | Summary details | Acceptable (Y/N) Internal Use Only | Comments / remedial actions Internal Use Only |
| Dimensions |  |  |  |  |
| Length (m) |  |  |  |  |
| Width (m) |  |  |  |  |
| Depth to base – maximum (3m) |  |  |  |  |
| Longitudinal base slope (1 in ?) |  |  |  |  |
| Cover level – is the cover level over the GCS between a minimum of 500 mm and a maximum of 1000 mm? |  |  |  |  |
| Geometry of GCS – is the shape cuboid? |  |  |  |  |
| Distance – from the nearest structure and land boundary, is there a minimum of five metres of clear open public space around the GCS both above and below? |  |  |  |  |
| Inflows |  |  |  |  |
| Provide a description of the contributing catchment land used and its size (m²) (industrial/commercial to be noted) |  |  |  |  |
| Sedimentation control – design details of the silt trap provided? |  |  |  |  |
| Any other upstream SUDS treatment to reduce sedimentation (Y/N); if yes, details provided? |  |  |  |  |
| Any Planting – as per SfS Appendix XIII |  |  |  |  |
| Outfall Arrangements |  |  |  |  |
| Flow control MH flow rate (l/s) |  |  |  |  |
| Flood route plan provided |  |  |  |  |
| Storage |  |  |  |  |
| Storage sizing – evidence that system has been sized to 1:30 year return period plus 15% loss of storage? |  |  |  |  |
| Structural |  |  |  |  |
| Confirm type of unit or structure to be used (manufacturer + product type) + BBA certification |  |  |  |  |
| Design life – data sheet or written confirmation from manufacturer provided? (60 year minimum) |  |  |  |  |
| Groundwater level (m) and flotation – groundwater table levels supplied; confirm if GCS is affected by groundwater. If yes, flotation calculations and mitigations must be provided and confirmed. |  |  |  |  |
| Confirm that calculations are provided to demonstrate acceptable structural capacity over the proposed system design life that are approved by an engineer |  |  |  |  |
| Has sufficient venting been provided to allow excess air pressure to be released when the GCS units fill? |  |  |  |  |
| Critical materials and product specifications |  |  |  |  |
| Geomembrane |  |  |  |  |
| Topsoil spec confirmed |  |  |  |  |
| Vehicle Access |  |  |  |  |
| Accommodate a 32 tonne tanker (load rating) |  |  |  |  |
| Reversing only for parking purposes (to be considered on a site-by-site basis) |  |  |  |  |
| Access adjacent to the GCS and not over any part of the structure |  |  |  |  |
| Full swept path analysis provided |  |  |  |  |
| Parking within 20 metres of silt trap and flow control manhole |  |  |  |  |
| Surface finish confirmed (provide detail) |  |  |  |  |
| Maintainability |  |  |  |  |
| Confirm that access for maintenance is acceptable |  |  |  |  |
| Can the GCS be jetted? (product data sheet from manufacturer to confirm) |  |  |  |  |
| Can the GCS be CCTV inspected? (product data sheet from manufacturer to confirm) |  |  |  |  |
| Are there any specific features that are likely to pose maintenance difficulties? If yes, identify mitigation measures required |  |  |  |  |